## Slide 1: GMP SUPPLEMENTARY TRAINING MODULE WATER FOR COSMETIC USED
Prepared by :
Haryanto Susilo - Indonesia
Surachai Piyayodilokchai - Thailand
Stephanie Wong Choong Moy - Malaysia
Approved by :
Asean Cosmetic GMP Team
Notes: This training module on Water for Cosmetic Manufacturer is a supplement to the series of the ASEAN GMP Training Modules
This supplement training module can be modified to fit a needed training programme depend on the experiences and knowledge of the audiences
The presentation will need around 60 – 90 minutes
The group session (optional) 45 minutes
Test paper (if necessary) 45 minutes

## Slide 2
Introduction
Water contaminants
Sources of water
Water treatment
Water purification engineering
Water testing
Inspection of water treatment plants
References
CONTENT OF PRESENTATION

## Slide 3
INTRODUCTION

## Slide 4
To define the type of water used as the main component of the cosmetic formula with the right quality with respect to the chemical and microbiological content to prevent cross contamination.
OBJECTIVE
Notes: To provide an introduction to Water for cosmetic Use. Water has unique chemical properties, and is able to dissolve, adsorb, absorb or suspend many compounds. These contaminants need to be removed before water can be used as an ingredient.
To review the ASEAN GMP Cosmetic guidance on water and water treatment.
To identify suitable sources and types of water for cosmetic use. Water has many uses in cosmetic manufacturing. The higher the risk of the cosmetic product, the more the water purity is paramount.
To briefly touch on bulk raw water storage and its problems, and then on any necessary steps for pre-treatment of water.
To review the type of equipment needed for pre-treatment of water. Pre-treatment of water may be needed before it can be purified sufficiently for cosmetic use.

## Slide 5
Like any starting material, water must conform to Good Manufacturing Practice
It must be “potable” and minimally comply with the quality of the national standard of drinking-water
Systems must be properly maintained to avoid contaminants
Specifications and periodic testing is required
Monitoring record is needed
BASIC PRINCIPLES
Notes: <number>
<footer>
<header>
<date/time>
Water must be “potable” before being purified in order to manufacture cosmetic products
Water is susceptible to bacterial contamination, and so,
Water purification systems should be properly validated and operating procedures developed to maintain control.
Water systems may have the potential for pyrogen and endotoxin contamination.
Appropriate specifications (physical, chemical and bacteriological) need to be established for chemical and microbial quality. The specifications may vary depending on the source and use of the water. Periodic testing is required. The frequency will depend on the source, validation and history of the system.
Testing record is required to show control.

## Slide 6
Types of water used in cosmetic processes are as follows:
For product:
  Tap water conforming to national standard
  Purified water (deionized, reverse osmosis) for cosmetic production
  For cleaning:
  Softened water
  For rinsing: same quality as for the product
  Water for final Rinse
  For sanitation:
  Steam
WATER TYPE
Notes: <number>
<footer>
<header>
<date/time>
Several kinds of water are needed during cosmetic production can be described as follow:
The most common type of water in use in a cosmetic factory is purified water. Purified water treatment such as deionisation, distillation or filtration depends on product requirement.
Besides potable water, there is softened water, which has had its Calcium and Magnesium removed. Such a water can be used e.g. for first washing steps. Certain processes require special well-defined qualities of water.
“Water for Final Rinse” is used for rinsing equipment after washing. It must be of the same quality as the water used for manufacturing the product.
Steam for sanitation purposes.

## Slide 7
WATER
CONTAMINANTS

## Slide 8
No water is free from contaminants
Contaminant groups:
  Chemical compounds
  Physical compounds
  Solids
  Gases
  Micro-organisms (algae, protozoa, bacteria)
Mineral contaminants :
  Calcium and magnesium
  Iron and manganese
  Silicates
  Carbon dioxide
  Hydrogen sulfide
WATER CONTAMINANTS (1)
  Phosphates
  Copper
  Aluminium
  Heavy metals
  Nitrates
Notes: <number>
<footer>
<header>
<date/time>
Contaminants of water:
Because of the wide variation in source and because of water’s unique chemical properties, which makes it the “universal solvent”, there is no pure water in nature. A wide variety of compounds may be present. There are more than 90 possible unacceptable contaminants of potable water listed by health authorities. The trainer can expand on other contaminants that are important, or on any local requirements that are relevant. For example, in some areas hormone-like compounds may be a problem.
Contaminants can be put into the following groups:
Inorganic contaminants, such as chloramines, magnesium carbonate, calcium carbonate and sodium chloride;
Organic contaminants, such as detergent residues, solvents and plasticizers;
Solids, such as clays, sols, cols and soils;
Gases, such as nitrogen, carbon dioxide and oxygen; and
Micro-organisms. These can be particularly troublesome because of the numbers that can grow in nutrient-depleted conditions. Bacteria may even multiply in pure water.
Contaminants of minerals:
Calcium and magnesium are probably the two most common mineral contaminants. They cause water hardness discussed in another slide. Heating or boiling water can precipitate these minerals leaving behind a scale deposit.
Iron and manganese discolour water and can react with drug products, or act as catalysts in decomposition processes.
Silicates may interfere with distillation equipment.
Carbon dioxide picked up in the atmosphere can change the pH and hence the conductivity of water. Carbonates can cause precipitation of calcium, and carbonic acid can cause corrosion of water treatment systems.
In areas of thermal activity, the water may be contaminated with sulphides, which even at low levels cause a rotten egg odour.
Phosphates can also cause precipitation of metal ions and scaling, e.g. in boilers.
Copper contamination can arise from corrosion of copper piping.
Aluminium can pose a problem in the manufacture of dialysis products. It can be introduced from the flocculation treatment used to reduce sols and clays.
Heavy metals (such as lead, arsenic, cadmium), particularly arsenic, may be problematic in wells in certain areas. Lead contamination can arise from tanks which have had lead solder repairs. Lead pipes are not recommended. Cadmium can also be an issue depending on the where the aquifer percolates.
Nitrates are an increasing problem for drinking water, but are easily removed by de-ionizers.
Contaminants of micro-organism
One of the major obstacles to successful treatment of water is the presence of micro-organisms. These are usually found in biofilms that develop on wet surfaces in almost any condition.
The major groups of contaminating micro-organisms are:
Algae: These arrive from raw water but can also grow where water is uncovered and there is a light source. Sometimes algae grow when UV lights lose their lethal effect and are emitting only visible light.
Protozoa: These include Cryptosporidium and Giardia. They can usually be easily filtered out since they are relatively large organisms.
Bacteria, such as Pseudomonas, Gram negative, Escherichia coli and coliforms. Of these, the normal aquatic microflora cause the most problems. Most of these belong to the Pseudomonas family or are Gram negative, non-fermenting bacteria. Some of them easily pass through 0.2 micrometer filters and are known to cause disease. Other Gram negative bacteria that are objectionable are Escherichia coli and coli forms. These are indicator organisms pointing to faecal contamination.

## Slide 9
WATER CONTAMINANTS (2)
Treatment depends on water’s chemistry and contaminants such as:
Rainfall
Erosion
Pollution
Dissolution
Evaporation
Sedimentation
Decomposition
Notes: The type of treatment is influenced by the impurities in water. These vary because of effects such as:
Rainfall, which can dissolve acid from the atmosphere and pick up other contaminants, such as fouling from roofs upon which it collects;
Erosion, which introduces minerals, clays and soils;
Pollution, from the atmosphere and from groundwater contamination;
Dissolution, whereby minerals and solids slowly dissolve in the stored water;
Evaporation, which can concentrate and precipitate minerals;
Sedimentation, whereby dissolved minerals re-precipitate and block pipes and filters;
Decomposition, for example when contaminants arise from degraded pollutants.

## Slide 10
TURBIDITY
Turbidity may come from:
Silt, clay, and suspended materials
Small particles include "colloids"
Notes: Turbidity:
Turbidity means the water is not clear.
Silt, clay, and suspended material cause turbidity, which is almost impossible to efficiently filter.
These small particles include "colloids”, which carry a slight negative electrical charge.
Removal of colloids is the first step in water treatment. This is usually accomplished by flocculation. This is not usually something that cosmetic manufacturers undertake unless they are sourcing their own water from dams, wells or rivers. Flocculation is usually carried out at the city water works, but if this is not the case, then it must be done by the cosmetic manufacturer.

## Slide 11
Water hardness classification
mg/L or ppm
as CaCO3
Soft
0-60
Moderate
61-120
Hard
121-180
Very hard
> 180
WATER HARDNESS
Notes: Hardness:
Hardness of water is due to the presence of calcium and magnesium salts. The concentration of these salts makes water “hard” or “soft”. Hardness is expressed as mg/l or ppm of Calcium Carbonate (CaCO3).
Very hard water has the potential for forming scale in equipment, especially if evaporation occurs, for example, in boilers.
Hard water must be softened before further treatment, since the calcium and magnesium salts can interfere with other purification processes. Removal is usually by water softeners that exchange the calcium and magnesium for sodium. Sodium salts are more soluble than calcium and magnesium salts, which can precipitate to form scale, or which can chelate drug products. Sodium is later removed in the de-ionizer or reverse osmosis units.

## Slide 12
Source of raw water
Rain water
Surface or ground water
Well or borehole
Municipal or civil – “tap water”
Purchased in bulk
WATER SOURCES
Notes: <number>
<footer>
<header>
<date/time>
Source of raw water:
The following are convenient, but not always acceptable, sources of raw water
for cosmetic use:
Rainwater: Although rarely used, it is sometimes collected from roofs and stored before use. Because it can be contaminated (due to fouled water collection surfaces) or acidified (due to atmospheric pollution), it must be subject to treatment and should not be regarded as pure or equivalent to distilled water.
Surface or ground water from rivers, dams, ponds or lakes: These are all subject to seasonal flow and quality varies between drought and flood years.
Well water or subterranean water: This is an important source for many factories where municipal water is not available. Common well water problems are described in the following slides in this module.
Municipal or civil: These are usually large scale civil works where the water is reticulated to homes and factories. Sometimes reliable, reticulated water may not be available in developing countries.
Water purchased in bulk: This requires vendor assessment and certification, as would be the case for any other purchased starting material. The delivery vehicle should be confirmed to be acceptable for the delivery of potable water.
Water from variable sources requires more stringent or complex treatment before cosmetic use.

## Slide 13
Well construction
Inspect exposed parts of the well
Depth of well
Check:
Nearby septic systems
Hazardous materials usage (pesticides, fertilizers, etc)
“Potability”
Well maintenance
WELL WATER
Notes: <number>
<footer>
<header>
<date/time>
Well water:
Some cosmetic manufacturers need to draw water from wells or bore holes. Some manufacturers feel they have better control of water from their own wells than from a municipal source. The aquifer that the well taps into may be contaminated, or the construction materials of the well could contribute to contamination.
Check points :
The exposed parts of the well should be inspected periodically for cracked, corroded, or damaged casing, broken or missing well caps, and settling and cracking of surface seals.
The depth of the well should also be determined – the shallower the well the greater is the chance of contamination from surface contaminants.
Check:
The location of nearby septic systems (which could contribute coliforms or faecal bacteria).
If there are hazardous materials used nearby. Sometimes these are disposed of in nearby septic systems. Hazardous materials include:
  Pesticides – farmers in areas near the well could use pesticides, which can permeate through the aquifer.
  Fertilizers, such as nitrates and phosphates, can be troublesome to remove and can encourage the proliferation of micro-organisms, especially algae if there is any light available.
  Herbicides – organophosphates can enter the aquifer.
  Fuels, such as diesel and petrol spills can also be problematic.
Testing records to show water is “potable”.
Records of well maintenance. The manufacturer must have procedures such as disinfection procedures or sediment removal, together with the use of any chemicals in the well. Chemicals that can leach include the oils used to lubricate the pumps.

## Slide 14
STORAGE
OF WATER
Notes: <number>
<footer>
<header>
<date/time>

## Slide 15
May be required prior to pre-treatment
Check material of construction
  concrete, steel are acceptable but check corrosion
  plastics or plastic linings may leach
Check cover
  to keep out insects, birds and animals
Check disinfection practices
RAW WATER STORAGES
Notes: <number>
<footer>
<header>
<date/time>
Large scale storage:
Raw water storage may be required according to local circumstances, such as intermittent water supplies.
Storage can be typically in cisterns or reservoirs made of concrete or tanks made of steel. Sometimes plastic or rubber bladders are used but these can cause significant problems with leachates and odours. Check the material of construction:
  Concrete and steel are acceptable, but check corrosion;
  Plastics or plastic linings may leach plastizisers such as phthalates.
The storage must have adequate cover to keep out insects, birds and animals. However, an air filter is not usually necessary. The quality of the raw water in this type of storage needs to be periodically checked and a physical inspection carried out.
Disinfection of the water is required. This is usually with chlorine at concentrations of 1 – 2 ppm. The chlorine levels need to be checked periodically. The storage tanks should be covered because the chlorine may have a life of only a few hours, and algal blooms may be encouraged if water is exposed to sunlight. UV lights suspended in these tanks are not effective bactericides. Periodically the tank should be emptied and cleaned.

## Slide 16
THE WATER TREATMENTS

## Slide 17
WATER TREATMENT GUIDANCE
The following should be monitored :
Sources of water
Treatment procedures
Water treatment equipment
Monitoring records required
Water treatment guidance
All water-treatment systems should be subject to:
  planned maintenance
  verified
  monitoring
Maintenance work should be documented
Notes: <number>
<footer>
<header>
<date/time>
The water sources, water-treatment equipment, and treated water should be monitored regularly for chemicals, biological contamination, and contamination by endotoxins, to ensure that the water complies with the specifications appropriate to its use.
Records should be maintained of the results of the monitoring and of any action taken.

## Slide 18
1. Disinfection ( i.e. chlorination )
2. Flocculation/coagulation (i.e. by alum)
3. Filtration through multi-media filter (gravel-sand-carbon) to 10 micron
4. Filtration through filter size of 1 micron
5. Re-disinfection (i.e. chlorination to eliminate germs)
PRE-TREATMENT GUIDANCE
Notes: <number>
<footer>
<header>
<date/time>
Filtration is a typical water pre-treatment system involves several steps, from physical removal of impurities to chemical treatment.
  Water is passed through coarse filters or screens to remove sticks, leaves and other large objects. Sand and grit settle out of the water during this stage.
  Next is filtration with a multi-media filter.
  The different media types are effective at removing suspended solids at sizes as small as 5 to 10 micrometers.
Some manufacturers may simply use a sand filter. All these filter types need to be periodically back-washed.
Flocculation, coagulation, and sedimentation are the subsequent treatments. During coagulation, aluminium or iron sulphate is added to the raw water, forming sticky elements that attach to small particles made up of bacteria, silt and other impurities. This “floc” sinks. This is called flocculation, sedimentation and clarification.
Manufacturers who source their own water should have as a minimum screens and sand filters before further purification. Desalination is sometimes used by manufacturers to remove sodium chloride if only brackish water is available.
Softening, to remove “hardness” due to calcium and magnesium, is covered in greater detail in some of the following slides.

## Slide 19
Activated-Carbon (AC) Filtration or Bisulphite
CHLORINE REMOVAL
raw water in
« S” trap to sewer
Water is kept circulating
to water softener & DI plant
cartridge
filter
5 micrometers
activated
carbon
filter
spray ball
break tank
air break to drain
centrifugal pump
air filter
float
operated
valve
sand
filter
excess water recycled
from deioniser
NOTE :
AC removes chlorine but bacteria can then grow
AC filtration can remove organic impurities
Bisulphite leaves sulphate residues but is anti-microbial
Notes: <number>
<footer>
<header>
<date/time>
Dechlorination of municipal water (or where chlorine is added to storage tanks) needs to be done; with either activated carbon (AC) filtration or bisulphite injection.
While AC filters reduce chlorine levels, the carbon provides an environment which is conducive to the growth of micro-organisms because of the huge surface area and the ready availability of nutrients. The carbon bed should be sanitised daily if possible. At a minimum, the bed should be sanitised weekly. Steam is useful for disinfecting the AC filters.
AC filters are also useful in removing organic contaminants.
The advantage of using bisulphite is that it does not facilitate microbial growth as does an AC filter. It is also less costly than AC. When bisulphite is injected into the process stream, it is oxidised to sulphate, and it also reduces free chlorine to the chloride ion. The by-products, sulphate and chloride, are removed or reduced by a de-ionizer or an RO system. Note that bisulphite does not remove organic contaminants, whereas AC does remove organic contaminants.
This above schematic drawing illustrates a typical storage and preliminary treatment system for water. Raw water arrives into a buffer or break tank via a level controlled valve. If there are further stages of treatment (such as DI or RO), the tank does not, generally, have to have sophisticated spray balls or air filters.
The water is pumped through a sand filter to remove large particles. This filter must be fitted with a back-flush facility, not shown here. The water then enters an activated carbon (AC) filter which removes organic impurities and chlorine. The AC filter can become heavily contaminated with bacteria. There should be some means of sanitizing it, such as a steam supply. Chemicals are generally not used to disinfect activated carbon filters. The water is then “polished” through a 5 micron filter before it enters the next treatment step. If there is no demand for the water it must be re-circulated to the buffer tank.
Water that is kept constantly circulating is less likely to grow bacteria, because they cannot settle and form a “biofilm”. All equipment such as pumps, pipes and tanks should be stainless steel wherever possible. Plastic should be avoided. Plasticizers may leach and this can result in out-of-specification Total Organic Carbon (TOC) levels. Adhesives used for welding plastic pipes may also leach into the water and cause problems.

## Slide 20
brine and salt tank
brine
"hard" water
in
zeolite water softener
exchanges
Ca and Mg for Na
drain
"soft" water to deioniser
by pass valve
WATER SOFTENER
Notes: <number>
<footer>
<header>
<date/time>
This schematic drawing give the description of system to reduce the hardness of water by removal of calcium and magnesium salts.
Water is softened in a zeolite exchange column where the calcium and magnesium ions are exchanged for sodium. The sodium then has to be removed by de-ionization or reverse osmosis. When the zeolite reaches its exchange limit, it needs to be stripped of calcium and magnesium. This can be done using a brine solution, which exchanges sodium for calcium and magnesium, and the cycle starts again.
The inspectors should ensure that there is a proper procedure for the regeneration of the unit, and that the system is properly monitored and sanitized. The frequency of regeneration is something that the inspectors should ask the manufacturer to justify.

## Slide 21
Water treatment room
External raw water storage
WATER TREATMENT COMPLEX
Notes: These photographs illustrate initial raw water storage and softening.
The top photograph shows a large scale storage tank, with automatic chlorine dosing.
The right photograph shows a water pre-treatment room with a water softener in place. In the foreground is the zeolite exchange column and in the background are the brine tanks used to recharge the zeolite column. The equipment is well laid-out, and the water treatment room looks well-organized and clean. There do not appear to be any leaks from pumps or pipes. Please note it is important that equipment is tagged, lines are marked and labeled with direction of flow and instruments are calibrated.
These rooms do not need to be environmentally controlled or the surfaces prescribed, but in this example the surfaces are smooth and impervious, which assists cleaning. The lighting levels should be good, allowing easy checking of instruments, recording of data and maintenance of equipment.

## Slide 22
WATER
PURIFICATION
ENGINEERING
Reverse osmosis system

## Slide 23
To examine the basic technology and requirements for:
Water treatment systems
Storage requirements
Sampling and testing
Microbial limits, disinfection
OBJECTIVES
Notes: <number>
<footer>
<header>
<date/time>
Water purification engineering objectives are to acquire an understanding of the basic design, technology and requirements for water treatment systems needed to ensure water is sufficiently pure for cosmetic use. In addition we will examine the various types of water treatment methods such as deionization, reverse osmosis, ultrafiltration and distillation.
If the purified water is not generated at the “point-of-use”, it needs to be stored. Post-treatment, small scale storage requirements are reviewed.
Next, there are slides on the special samplig and testing requirements for water, and the different specifications of water used in cosmetics.
Microbial limits and disinfection methods for water treatment systems are also discussed.

## Slide 24
There should be:
proper pipe slope to avoid stagnation and can be drained easily;
Proper fittings & connections that can be easily cleaned and sanitized;
constructed of suitable materials such as polyethylene material, stainless steel, etc.
water circulation
non-return valves (NRV)
WATER SYSTEM DESIGN
Notes: <number>
<footer>
<header>
<date/time>
Water system design:
Much of the chemical and physical aspects of water system design are relatively straightforward. However, a significant part of good water system design is ensuring that microbial contamination is minimized. Microbial contamination can arise as a result of colonization of surfaces and stagnant areas by aquatic bacteria with the formation of biofilm. If the bacteria can be prevented from sticking to the surfaces, the battle is almost won. Smooth surfaces, moving water and no dead spots, all are good design elements.
Ensure pipes are sloped so water does not pool and lines can be completely drained. Installation records should include a pipe slope check.
Sanitary fittings and connections should have no crevices for bacteria to colonise.
Piping and fittings should be constructed of suitable materials such as stainless steel or special polypropylene tubing in order to prevent bacteria from sticking to the surfaces. If pipes need to be joined, then orbital welding is ideal. Check that there are documented records of the welding seam and electropolished surfaces. Stainless steel quality needs to be specified i.e. 316L. Other stainless steel qualities can corrode. Grade 316L stainless steel can be checked using a magnet, since it is non-magnetic.
Circulating the water at high velocities prevents bacteria from adhering to surfaces and growing. The general guideline is that velocities should be above 2 lm/sec.
Incorporate non-return valves (NRV) that prevent backflow which could cause contaminated water to mix with clean water. These are sometimes called backflow preventers or check valves.

## Slide 25
Further water treatment purification stages downstream of the pre-treatment system :
Pre - disinfection - flocculation
Filtration
Softening column
Disinfection
De-ionization System
Reverse osmosis plus deionization
UV system
Looping of water
WATER PURIFICATION STAGES
Notes: <number>
<footer>
<header>
<date/time>
Water treatment purification stages:
Water needs to be further purified after the pretreatment phase discussed before.
Filtration is needed to remove particulates (that may have been shed by softeners and downstream equipment) and micro-organisms, which always tend to exploit any environmental niche.
Disinfection is necessary because water systems are required to be sanitary, but not sterile. The commonly used disinfection agents are heat, UV, ozone, chlorine, and peroxygen products.
Reverse osmosis (RO) or de-ionisation (DI) are the most common methods for preparing Purified Water that meets pharmacopoeia requirements for cosmetic manufacturing. Due to increased pharmacopeia requirements for resistivity, it is frequently necessary to have two consecutive RO treatments (two-stage RO), whereby the second RO passage can be replaced by a “continuous de-ionization” or “electro-de-ionisation” (CDI or EDI).

## Slide 26
There should be no dead legs
Water scours deadleg
If D=25mm & distance X is greater than 50mm, we have
a dead leg that is too long.
Deadleg section
<2D
Flow direction arrows on pipes are important
Sanitary Valve
D
X
WATER SYSTEM DESIGN (1)
Notes: <number>
<footer>
<header>
<date/time>
Water system design:
There should be no dead legs!
Stagnant areas allow microbial contamination as a result of colonization of surfaces with the formation of biofilm, as discussed in Part 1. Dead legs are stagnant areas where there is no water flow.
There do not appear to be any regulations which give a specification for dead legs. Deciding when a dead leg is unacceptable is therefore not easy, as it involves the respective diameters of the pipes and the velocity, but there is a consensus in the industry that a dead leg should not be greater than twice the diameter of the pipe.
If there are long runs of pipe to outlets without circulation, the cosmetic manufacturer must have a procedure in place which allows the pipework to be completely drained, left dry and sanitized or sterilized before use. This should be done on a daily basis. Special attention needs to be given to samples and test frequency for microbial counts from this type of outlet.
Check that the piping has direction arrows on it. If the flow is in the wrong direction through a fitting it will not “scour” the fitting, resulting in the formation of biofilm.

## Slide 27
3. The water is contaminated as it passes through the valve
2. In Ball valves, Bacteria can grow when the valves are closed
1. Butterfly valves are better than Ball valves
Stagnant water
inside valve
WATER SYSTEM DESIGN (2)
Notes: <number>
<footer>
<header>
<date/time>
Water system design: (Contd.)
Although ball valves can be used in the early stages of water treatment, they (and the related cone valve) should not be used in the water treatment system downstream of RO and DI outlets. This is because the “ball in socket” construction can be easily contaminated. Ball valves are not easy to clean unless dismantled. The space between the ball and the housing can be easily colonised by bacteria. Consequently, the water will become contaminated as it passes through the valve.
Valves that can be used include diaphragm valves (as long as the diaphragm is made of a suitable material, ideally teflon coated neoprene), and butterfly valves.
Zero dead leg valves are now available for high purity water systems.

## Slide 28
Cationic column
Anionic column
Hygienic pump
Outlets or storage.
Ozone generator
UV light
HCl
NaOH
Eluates to
neutralization
plant
Air break to sewer
Drain line
from water softener
Water must be kept circulating
1
2
3
4
5
6
1
2
3
4
5
6
Return to de-ioniser
Cartridge
filter 5 µm
Cartridge
filter 1 µm
DE-IONIZER SCHEMATIC
Notes: <number>
<footer>
<header>
<date/time>
This schematic drawing of a typical de-ionizer. Use it to explain the pathway of water through a twin bed de-ionizer.
Softened water enters at the top right into the twin bed de-ionizer. Cation and anion exchange agents are resins with large surface areas. Cations are exchanged for H+, anions for OH-, the combination is H-OH, or water! After Cation and anion exchange, the water is filtered (to remove resin particles and sometimes bacteria) before being re-circulated through the distribution system and returned to the de-ionizer, usually via a buffer tank. The Cation and anion resins are regenerated using hydrochloric acid and sodium hydroxide respectively. There should be specifications available for these two materials for the inspector to check.
Mixed bed de-ionizers are also common. They may be more prone to bacterial contamination and so the inspector should check them carefully.
They should be disinfected at regular intervals.
Heat is not a option, because of the resin material. Furthermore, many of the de-ionizers are made of plastic materials. However, the regenerating chemicals are very effective biocides and so the system should be regenerated frequently, at least once a week, regardless of the conductivity readings. Inspectors should ask for the sanitation records so that these can be checked.
Disinfection of the circulating water is necessary; this can be achieved by inline UV irradiation and or ozonization.

## Slide 29
DE-IONIZER OPERATION

## Slide 30
raw water
High pressure
Feed
water
under
pressure
Reject
water
Semi-permeable
membrane
Permeate
water
drain or recycle
Low pressure
Purified water
REVERSE OSMOSIS THEORY
Reverse osmosis may be used to:
purified water
feeding of distillation units or ultra-filtration units
water for final rinse
Notes: <number>
<footer>
<header>
<date/time>
High salt solutions will draw water from low salt solutions if they are separated by a semi-permeable membrane, until an equilibrium is achieved. The height of the column of water that results is the osmotic pressure. Conversely, if pressure is applied above the osmotic pressure, pure water will be driven the other way through the membrane. This is called reverse osmosis (RO).
Ions and particles are left behind in the reject water. Water is continuously passed over the membrane with the reject water being recycled or sent to drain. Although the “permeate“ is purified, it may need to undergo a second RO stage to meet pharmacopeia specifications, as far as resistivity is concerned.

## Slide 31
RO SCHEMATIC DIAGRAM
DRINE TANK

## Slide 32
Branch
Branch
2nd stage buffer tank
Cartridge
filter 1 µm
Second stage RO cartridge
First stage filtrate feeds second stage RO
with excess back to 1st stage buffer tank
.
1st stage reject concentrate
Air break
to sewer
Second stage reject water goes back to first stage buffer tank
Second stage RO water
meets Pharmacopoeia
standards
Outlets or storage
1st stage buffer tank
Water from softener or de-ioniser
Water returns to 1st stage buffer tank
Hygienic pump
First stage RO cartridge
High pressure
pump
2-STAGES RO SCHEMATIC
Notes: <number>
<footer>
<header>
<date/time>
This schematic drawing of a typical Reverse Osmosis (RO) system.
Use it to explain the pathway of water through a two-stage RO.
Softened water enters the 1st stage buffer tank and is passed under pressure (achieved by a series of hygienic pumps) across the membrane in the first stage cartridge.
The first stage filtrate feeds into the 2nd stage buffer tank. The 1st stage reject water is discarded, or can be collected and used, for example, for washing floors and walls.
Water from the 2nd stage buffer tank is forced under pressure across a 2nd series of membranes in the second stage RO cartridge.
The 2nd stage filtrate (also called the permeate) can be used for cosmetic manufacturing. It should be re-circulated through the distribution system and back to 1st stage buffer tank. The 2nd stage reject water is also returned to the 1st stage buffer tank.
RO Benefits:
In-line filters in both stages remove particulates.
However, the membrane may still foul, and so has to be back-washed periodically, usually on an automatic cycle. Bacteria can grow in the system, as well as on and through the membrane, so the RO system needs to be periodically sanitized. Because of the plastics used (eg. in the membrane), heat is usually not an option.
Some RO membranes can, however, be heat sanitized. Peroxygen products (such as hydrogen peroxide or peracetic acid) are preferred, but some membranes are able to tolerate chlorine.
Inspectors should ask for back-wash and sanitation records.

## Slide 33
Note :
Fm : Flow rate sensor with LCD display
FL : Flow indicator (rotametor)
COMBINED TREATMENT (1)

## Slide 34
Multi media column ~ detailed views
FRONT VIEW
SIDE VIEW
CUT VIEW
TOP VIEW
BOTTOM VIEW
COMBINED TREATMENT (2)

## Slide 35
Reservoir of incoming water
Reverse osmosis system
De-ionized water treatment
Treated Water in the storage tank
COMBINED TREATMENT (3)

## Slide 36: Typical water storage and distribution schematic diagram
Water must be kept circulating
Spray ball
Cartridge
filter 1 µm
Air break
to drain
Outlets
Hygienic pump
Optional
in-line filter
0,2 µm
UV light
Feed Water from
DI or RO
Heat Exchanger
Ozone Generator
Hydrophobic air filter
& burst disc
WATER STORAGE & DISTRIBUTION
Notes: <number>
<footer>
<header>
<date/time>
The storage of highly purified water types is critical because of the risk of re-contamination by micro-organisms and other contaminants. This schematic drawing is used to explain the design features of a good storage system.
Good design elements, not mentioned previously, include:
Closed system with continuous re-circulation at 1-2 (or more) linear metres per second;
Hydrophobic vent filters, which can be sterilized and integrity-tested;
Burst disc if tank is heated, to prevent the tank collapsing as it cools; Re- circulation via spray ball, to ensure the tank lid is wet with moving water;
In-line disinfection, by periodic heating, ozonization or UV;
Air breaks to drains;
In-line 0.2 micrometer filter to “polish” the water in purified water systems
WFI storage, which must be 70oC or above, and preferably above 80oC. (No ozone and filtration in WfI storage and distribution systems).

## Slide 37
Heat
One of the most reliable methods of disinfection of water systems
Ozone
Produced easily
Leaves no residue
UV
UV does not “sterilize”
Flow rate critical
Post-irradiation recontamination may be an issue
Lamps have short life
Other chemicals
Sodium Hypo-chlorite solution
DISINFECTION
Notes: <number>
<footer>
<header>
<date/time>
Heat:
Heat is the preferred disinfection method because it is safe, inexpensive, effective and leaves no residues.
Heat is one of the most reliable methods used to disinfect water systems, as the problem with chemical disinfectants is achieving a balance between the risks from microbial pathogens and disinfection by-products. It is important to provide protection from microbial pathogens while simultaneously ensuring that disinfection by-products do not affect the ultimate product.
The manufacturer must record the time and temperature of the heat disinfection cycle: > 60oC for purified water for 1 hour or > 70oC for WFI, continuous circulation. The contact time must be validated. The inspector should ask for records of this to verify effective contact time.
Ozone
The chemical formula is O3.
This gas is highly unstable, and is one of the strongest oxidizing agents.
It is easily produced by O3-promoting UV light units, or corona electricity through O2.
It leaves no residue. However, because it is highly reactive, O3 must be stripped from the water before the water is used to manufacture cosmetics. Otherwise it will quickly degrade the actives.
Ozone may be removed by ultraviolet (UV) light at 254 nanometers, reducing the ozone to oxygen. The use of Ozone in storage and distribution systems is growing because of its relatively low capital and operating costs, compared to hot water generation and storage.
UV light:
UV light is bactericidal, but water can attenuate the radiation quickly. The design and maintenance of the system is important. The units do not “sterilize” water as is sometimes claimed; at best the manufacturer can expect about a 3 log reduction of bacteria for properly installed and maintained equipment. The lamp life is often less than 12 months.
Flow through the unit must be turbulent, in a thin layer, and the dwell time must allow the bactericidal effect to be exerted.
Some organisms have efficient UV repair mechanisms, and so sub-lethally damaged organisms can grow again if they pass through the unit too quickly. They can then colonise the water treatment system downstream of the UV light unit, causing considerable problems.
The lamp intensity decays with lamp life and can become ineffective. The wavelength can also vary with lamp life. In addition, the units can become contaminated downstream of the lamp.
Desinfection – other chemicals
XO2 – the Peroxygen family of hydrogen peroxide, peracetic acid, and peroxitane. Like all additives to the water supply, they must have documented specifications, they must be sourced from QC-approved suppliers and records must be kept of their use.
The halogen family of chlorine, bromine and chloramines is very strong, and these chemicals are very good disinfectants. However, residues can cause considerable corrosion. The by-products of halogen chemical disinfectants can cause problems if they are not completely removed from the water.
Formaldehyde is the principal agent from the aldehyde family, but glutaraldehyde has also been used. The latter has a toxic vapour even at very low levels so its use is not widespread. The aldehydes have persistent residues which can take so long to flush out of the water that the system becomes re-contaminated. Ensure that the company conducts tests for residues before the water is used for manufacturing.

## Slide 38
WATER TESTING

## Slide 39
There must be a sampling procedure
Sample integrity must be assured
Sampler training
Sample point
Sample size
Sample container
Sample label
Sample storage and transport
Arrival at the laboratory
Test record
WATER SAMPLING
Notes: <number>
<footer>
<header>
<date/time>
Sampling:
There must be a sampling procedure.
The sample integrity must be assured. The sample received in the laboratory must reflect the bulk water’s physical, chemical, and biological quality. Because of water’s solvent properties and the nature of micro-organisms, this can change very quickly. For example, the microbe population in ideal circumstances can double or triple every hour. Microbes can grow at very low temperatures and in extremely low nutrient levels. Even distilled water may have enough nutrients to support organisms such as some of the pseudomonas species.
The persons who take the sample should also have training on aseptic handling practices, to ensure that they do not contaminate the sample while it is being taken.
The sample point should be hygienic and the practice of flushing it, or not, should follow manufacturing practice. Sample points for subsystems, such as de-ionizers and RO’s, should be as close to the downstream side as possible in order to reflect the quality of the water being fed to the next subsystem. All water outlets in the factory should also be checked periodically. This should be done unannounced, if possible, so that water can be sampled through any attachments to the outlet, such as hoses or pumps.
Sample sizes of at least 100 – 500mL are required; samples of 1 or 2 mL are unacceptable.
The sample container should be sterile, inert, and able to be securely closed. Plastic containers that are re-sterilized sometimes distort in the autoclave, so that the quality of recycled containers should be carefully checked. Some plastics may leach and thus affect tests such as the TOC test. Single-use, sterile, inert plastic bags are available. However, these could prove too expensive for some manufacturers to consider.
The container must be properly labeled. The label should have the date, time and location sampled as well as the sampler’s name or initials. It must be attached firmly to the container. Felt tip permanent markers are satisfactory but may leach solvent if used on plastics, and may thus affect the TOC test. It is important for the label to be properly removed should the container be recycled.
Unless tested within a few hours, the sample should be chilled to less than 8oC, but not frozen. Samples from heated water systems should be rapidly cooled. If a sample is to be transported to a remote laboratory, refrigerated packing must be allowed for to ensure that the sample stays cool. Inclusion of a temperature data logger is good practice.
On arrival at the laboratory the condition and temperature of the sample should be noted, as this may be important if an out of specification result needs to be investigated. It is good practice to have a sample registration and tracking system.
The laboratory should record the time at which microbial testing started.

## Slide 40
Basic principle of water testing are as follows:
Method verification
Chemical testing
Microbiological testing
  test method
  types of media used
  incubation time and temperature
  objectionable and indicator organisms
  manufacturer must set specifications
THE WATER TESTING
Notes: <number>
<footer>
<header>
<date/time>
Testing:
Method Verification - The methods must be validated or verified in the laboratory, even if they are pharmacopoeial methods.
Chemical testing - Chemical testing follows normal laboratory practices. However, TOC requires sophisticated, expensive equipment and trained technicians, which may put it beyond the reach of some manufacturers.
Microbiological testing - It is important that microbiological testing be conducted in a well-equipped laboratory with adequate resources.
  Method: The common methods for microbial total count are Most Probable Number Test (not reliable for low numbers), Spread or Pour Plate (can only test only 1 or 10mL respectively; not reliable for low counts) or membrane filtration, which is preferred.
  Media: There are various types of test media that can be used.
  Incubation time and temperature: Preferably 32oC or lower (higher temperatures than this inhibit aquatic microflora) and up to 5 days (sub-lethally damaged organisms may not revive quickly).
  Objectionable and indicator organisms: Any organism which can grow in the final product, or can cause physical and chemical changes to the product, or is pathogenic, is unacceptable in purified water. Indicator organisms, such as Escherichia coli or coliforms, point to faecal contamination. They “indicate” possible contamination by other pathogenic organisms.
  The manufacturer must set specifications for total count and absence of objectionable and indicator organisms. The USP recommends a limit of 100 total aerobic microbial colony-forming units (CFU) per mL for purified water.

## Slide 41
WATER SPECIFICATIONS
DESCRIPTION
Ph.Eur.
USP
JP
Color
Clarity & consistency
Odor
pH
5.0 - 7.0
-
Cl
< 0.5
-
pass test
SO
4
past test
-
pass test
NH
4
< 0.2
-
< 0.05
Ca / Mg
pass test
-
-
Nitrates
< 0.2
-
pass test
Nitrites
-
-
pass test
Conductivity (µS/cm)*
-
< 1.3
-
Oxidizable subs
pass test
-
pass test
Solid (ppm)
< 10
-
< 10
TOC (ppb)
< 500
< 500
Colorless
Clear liquid
Odorless
* For cosmetic used 5-7
-
Notes: Water specifications :
The manufacturer must set specifications for all water types used in the factory in connection with the production of cosmetic products for:
  cleaning,
  washing,
  rinsing and
  for use in the product.
The chemical and physical specifications from the Pharmacopoeias are based on the assumption that potable water, which already meets WHO standards, is used as the raw water for further purification.
The table shows a comparison of four major pharmacopoeia requirements: the European, Japanese, and United States.
  A dash indicates that there is no test requirement in that compendium.
  units are mg/L unless otherwise specified.
  Some limit tests do not have units.
  Note that the JP requirement for ammonium ion is much more stringent than the Ph Eur, which does not require nitrite testing.
  The USP focuses on total organic carbon (TOC), in combination with conductivity and pH, which replace the battery of other limit tests . TOC can be measured on-line and is becoming more popular because, in combination with conductivity, it can replace laborious chemical testing. pH, TOC and conductivity are non-specific assays, measuring every analyze which contributes hydrogen ion, ions in general or organic carbon.
  The JP requires TOC in addition to maintaining the other limit tests.

## Slide 42
Sampling location
Target
Alert
Action
Raw water
200
300
500
Post multimedia filter
100
300
500
Post softener
100
300
500
Post activated carbon filter
50
300
500
Feed to RO
20
200
500
RO permeate
10
50
100
Points of Use
1
10
100
BACTERIAL LIMITS
Suggested bacterial limits (CFU /mL)
(no E-coli form bateria,no pathogenic bacteria)
Notes: Sampling locations and limits for microbiological testing:
The limits are not from any official literature and are thus intended merely as a guide.
The table is a suggested list of sampling locations and limits (for total aerobic microbial plate count).
Note that in some countries, the “Action” required if out of specification results are detected may well include recall of therapeutic goods even if they meet finished goods specification. This is because the water treatment system is seen to be out of control.
Prudent manufacturers should react promptly to “alert” limits so that the system remains in control.
CFU = colony forming units

## Slide 43
INSPECTION
OF
WATER TREATMENT
PLANTS

## Slide 44
Procedure for cleaning and sanitization of water treatment system should be available and with defined written procedure which may consist of the following:
  frequency
  cleaning agent
  sanitizing agent
  acceptance criteria
  documentation
CLEANING & SANITATION

## Slide 45
Conducting the inspection
Take the schematic diagram and walk around the entire system
Check:
  dead legs
  filter
  pipes and fittings
  DI
  storage tanks
  by-pass lines
  pumps
  UV lights
  sample points
  RO
  non return valves
  heat exchangers
INSPECTION (1)
Notes: <number>
<footer>
<header>
<date/time>
The inspection:
After the desk top review, it is important to go into the factory and walk around the entire system.
Check equipment against the drawings.
Equipment such as valves and pumps should be tagged with unique numbers, linking to the numbers on the drawings.
Check dead legs, pumps, filter, UV lights, pipes and fittings, sample points, DI & RO units, storage tanks, non-return valves, by-pass lines and heat exchangers.
Note that these are examples only; there may also be other points to check, for example, burst discs or rupture discs and venting filters on water storage tanks, which prevent the tank collapsing if a vacuum is formed.
Identify equipment numbers and ask to see individual installation and operational qualification, and maintenance records.

## Slide 46
Check:
stainless steel, PE, PP pipelines are appropriate outside the storage tanks and mixing room.
storage tanks and mixing room,the pipelines should be appropriate and stable material i.e.stainless steel
welding quality (right welding material)
hygienic couplings (stainless steel)
passivation
air breaks or “Tundish”
INSPECTION (2)
Notes: <number>
<footer>
<header>
<date/time>
Inspection: (Contd.)
Check the construction. Is the system made of stainless steel? What is the grade of stainless steel? PVC and most plastics are not recommended because bacteria are easily able to colonise. Polypropylene PTFE (eg Teflon®) can also be used for purified water and systems if specifically designed for this use.
Check for:
Electropolished internal welds. Electropolishing is basically the opposite of electroplating, thereby smoothing the surface. The smooth surfaces help reduce bacterial colonization.
Hygienic couplings - no threaded fittings in the water flow which can become contaminated. Example on next slide.
"Passivation" records. Whenever equipment in contact with water is repaired or changed, passivation should be considered, especially for systems producing water of very high purity. Passivation is the removal of free iron from the surface of the steel. This is performed by immersing the steel in an oxidant, such as nitric acid or citric acid solution. Since the top layer of iron is removed, passivation diminishes surface discoloration. While passivation does not affect the thickness or effectiveness of the passive layer, it is useful in producing a clean surface for a further treatment.
No direct connections to drains or sewers, and that non-return valves and back-flow preventers are working or have been properly checked. Tundish is the engineering term for an air break to a fixed funnel, to prevent bacteria from a drain or sewer growing into the water treatment plant.

## Slide 47
Check pipes and pumps for
  hygienic couplings
  welded pipes
  hygienic pumps
  hygienic sampling points
  acceptable floor slope
  leaks
INSPECTION (3)
Notes: <number>
<footer>
<header>
<date/time>
Inspection: (Contd.)
Check pipes and pumps.
The photograph shows a good example of a neatly laid-out water treatment room with good equipment and pipes. There are hygienic couplings (Ladish® or Tri-Clover ® clamps), welded pipes and hygienic pumps. Note also hygienic sampling points.

## Slide 48
Staining on water storage tanks
Corrosion on plates of heat exchangers indicates possible contamination
Check condition of equipment
INSPECTION (4)
Notes: <number>
<footer>
<header>
<date/time>
Inspection: (Contd.)
Assess physical condition of equipment. Look for stains and leaks that could indicate problems.
Check to make sure heat exchangers are double tube or double shell. If not, there should be continuous pressure monitoring to ensure the heating or cooling liquid does not contaminate the pure water through any pinholes. For single plate heat exchangers, the pressure of the heating or cooling liquid must be LOWER than the purified water at all times. An exception may be where the liquid is of a higher purity than the water being produced.
Note from the heat exchanger example above that even high grade stainless steel, such as 318SS, can be subject to pit corrosion!

## Slide 49
Check maintenance records
Check maintenance of pump seals and O rings
INSPECTION (5)
Notes: <number>
<footer>
<header>
<date/time>
Inspection: (Contd.)
Check maintenance of the entire system by examining the maintenance procedure and records. For example, check the “O” rings of connections and the maintenance of the pump seals. The pump on the left shows good connections and a good standard of engineering.
The one on the right shows a threaded coupling, called a milk coupling or sanitary coupling. Threaded couplings and couplings in general should be avoided whenever possible.
Where welding is impossible, hygienic couplings should be used or milk (sanitary) coupling, which are acceptable since the threaded fitting is not part of the fluid pathway, and so should not contaminate the water.
The inspector must be satisfied that hidden seals and “O” rings have actually been removed, examined and/or replaced during maintenance.

## Slide 50
More points to check (Contd.)
UV light – monitoring performance and lamp life and intensity
Validating ozone dosage
Specifications for acids, alkalis for DI system and sodium chloride for water softener
“Normally open” and “normally closed” valves
INSPECTION (6)
Notes: <number>
<footer>
<header>
<date/time>
Inspection: (Contd.)
Further points to check:
UV light – monitoring performance and lamp life. The lethal radiant energy from UV lights drops off quickly, so many have to be replaced approximately every 6 months. Does the manufacturer have an hour meter and is the lamp replaced according to the supplier’s recommendations? Can the intensity of the light be measured?
Validating ozone dosage is difficult. It may be possible for the manufacturer to get the supplier’s validation studies showing worst case lethal effects.
Water softener sodium chloride specifications. Like any ancillary material, the salt, acids and alkalis used as consumables in water treatment plant should have purchase specifications. Note: testing is not required unless for trouble shooting purposes.
Check the drawings to see if valves are marked as “Normally Open” or “Normally Closed”, then physically check the valve position. It is surprising sometimes that valves are not returned to the correct operating position; for example, after de-ionizer regeneration.

## Slide 51
REFERENCES
ASEAN Guidelines for Cosmetic GMP (2003)
WHO EDM, Supplementary Training Modules on Good Manufacturing Practice, Water for Pharmaceutical Use, Part 1,2, and 3. (2001)
WHO, Guidelines for drinking-water quality, 2nd edition, volume 1 (1993)
WHO, Guidelines for drinking-water quality, 2nd edition, volume 2, (1996)
WHO, Guidelines for drinking-water quality, 2nd edition, Volume 3; (1997)
WHO, Guidelines for drinking-water quality, 2nd edition, Addendum to Volume 1 & 2 (1998)
Notes: The principles are contained in the Good Manufacturing Practices: supplementary guidelines for the manufacture of pharmaceutical excipients: WHO Expert Committee on Specifications for Pharmaceutical Preparations. Thirty-fifth report. Geneva, World Health Organization, 1999, Annex 5 (WHO Technical Report Series, No. 885). Pharmacopoeia monographs for water are published in the International Pharmacopoeia, 3rd Edition, Volume 4, 1999, pages 131-135.
Refer to the handout 2-1-3 for reference material which will give more information on suggested specifications for water. (This material is not included in the module):
WHO, 1993. Guidelines for drinking-water quality, 2nd edition, volume 1;
WHO, 1996. Guidelines for drinking-water quality, 2nd edition, volume 2, WHO, 1997. Guidelines for drinking-water quality, 2nd edition, Volume 3;
WHO, 1998. Guidelines for drinking-water quality, 2nd edition, Addendum to Volume 1;
WHO, 1998. Guidelines for drinking-water quality, 2nd edition, Addendum to Volume 2.

## Slide 52
Thank You